## Slide 1: Smoke control fundamentals design & testing 101 presented at the 54th ANNUAL CAFAA CONFERENCE FEBRUARY 9, 2024
Mark McQuaid
H.R. Kirkland Co.

## Slide 2: Smoke control system definition
The 2022 California Building Code (CBC), based on the 2021 International Building Code, defines a smoke control system in Section 909.1
  A system consisting of fans, dampers, and smoke barriers designed to provide a tenable environment for the evacuation or relocation of occupants
  It is not intended for the preservation of contents, the timely restoration of operations or for assistance in fire suppression or overhaul activities

## Slide 3: Applicable codes/standards
2022 California Building Code (CBC), Section 909
  Omits maintenance requirements
2022 California Fire Code (CFC), Section 909
  Maintenance requirements listed in Section 909.22
NFPA-92, Standard for Smoke Control Systems
  Referenced standard for air flow and exhaust means of mechanical smoke control
Underwriters laboratories, UUKL, Smoke Control System Equipment
  Includes requirements of ANSI/UL 864 Control Units for Fire-Protective Signaling Systems

## Slide 4: where required
Covered mall buildings with atriums
  CBC, Section 402.7
High-rise buildings
  CBC, Section 403.4.7
Atriums
  CBC, Section 404.5
Underground buildings
  CBC, Section 405.5
Group I-3 Windowless Buildings
  CBC, Section 408.9
Large stages
  CBC, Section 410.2.7

## Slide 5: Design requirements
Design starts with a Rational Analysis (Smoke Control Report) required by CBC, Section 909.4
  Prepared by a member of the design team (Typically a fire protection or mechanical engineering firm)
The rational analysis accompanies construction documents and supports:
  Types of systems to be employed
  Methods of operation (passive or mechanical)
  Construction methods
  Sequence of Operations

## Slide 6: Design requirements
Types of Smoke Control Systems
  Passive
  Mechanical

## Slide 7: Passive smoke control cbc section 909.5
Fire Doors
Fire/Smoke Damper

## Slide 8: Passive smoke control cbc section 909.5
Openings protected by automatic-closing devices
  Fire doors with door hold-open devices
  Fire and smoke dampers
Activated by controls described in the rational analysis, including:
  Smoke/heat detectors (fire doors and some dampers)
  Duct mounted smoke detectors (fan shutdown and dampers)
Not required to meet verification (positive status) requirements of CBC Section 909.12.1
  Subject to interpretation

## Slide 9: mechanical smoke control Pressurization cBC 909.6

## Slide 10: mechanical smoke control Pressurization
Pressurization - CBC Section 909.6
  Primary means of mechanical smoke control
  Tenable environment not required in in the zone of origin.
  Creates pressure differences across smoke barriers (typically 0.05” water gage)
  Maximum pressure difference limited by emergency door opening forces (30 pounds to set a door in motion and 15 pounds to fully open an emergency exit door)

## Slide 11: mechanical smoke control Exhaust CBC 909.8

## Slide 12: mechanical smoke control exhaust
Exhaust - CBC Section 909.8
  Used for large enclosed spaces, such as atriums or malls
  Must obtain prior approval from Authority Having Jurisdiction
  Design in accordance with NFPA 92 is required
  System must maintain the smoke layer at least 6 feet above the highest walking surface meant for egress within the smoke zone

## Slide 13: mechanical smoke control air flow CBC 909.7

## Slide 14: mechanical smoke control air flow
Airflow - CBC Section 909.7
  Prevents smoke migration through fixed openings
  Must obtain prior approval from Authority Having Jurisdiction
  Design in accordance with NFPA 92 is required
  Airflow toward the fire shall not exceed 200 feet per minute

## Slide 15: SMOKE CONTROL FUNDAMENTALS
INSPECTIONS
AND
TESTING

## Slide 16: Inspections and testing
CBC Section 909.3 Special Inspection and Test Requirements
  Smoke control systems shall undergo special inspections and tests sufficient to verify the proper commissioning of the smoke control design in its final installed condition.
  The rational analysis must detail procedures and methods to be used and the items subject to inspections and tests.
  Smoke control special inspections and scope are listed in CBC Section 1704 and 1705.19

## Slide 17: Inspections and testing
CBC Section 1704.2 Special Inspections and Tests
  The owner or the owner’s authorized agent, other than the contractor, shall employ special inspectors
  Special inspectors must provide written documentation to the building official demonstrating the competence and relevant experience or training
    Requirements include expertise in fire protection engineering, mechanical engineering and certification as air balancers.
  Registered design professionals and engineers of record who worked on the project can act as special inspectors provided their personnel meet the qualifications of the Building Official

## Slide 18: Inspections and testing
CBC Section 1705.19.1 Testing Scope
Requires inspections during the erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location
Also requires inspections prior to occupancy and after sufficient completion for the purposes of pressure difference testing, flow measurements and detection and control verification.

## Slide 19: Inspections and testing
…During erection of ductwork and prior to concealment for the purposes of leakage testing
Often performed by the mechanical subcontractor and air balance contractor
Reviewed by the special inspector for compliance with the specifications.
Part of the report issued by the special inspector
Fire alarm contractor generally not involved

## Slide 20: Inspections and testing
…Recording of device location:
Smoke control equipment
  Fans
  Dampers
  Other smoke control devices (rolldown doors, etc.)
Fire alarm initiating devices
  Smoke/heat sensors
  Water flow switches)
Verification devices (CBC Section 909.12.1)
  Differential pressure switches
  Damper position switches
  Service disconnects

## Slide 21: Verification devices damper position switch

## Slide 22: Verification devices damper actuator

## Slide 23: Verification devices differential pressure switch

## Slide 24: Verification devices variable frequency drive

## Slide 25: Verification devices current relay

## Slide 26: Verification devices power supervision

## Slide 27: Inspections and testing
…Pressure difference testing and flow measurements
  Performed by the air balance contractor and reviewed by the special inspector.
  Primarily involves mechanical and controls subcontractors
  Fire alarm contractor indirectly involved to initiate the sequence of operations and report device status from the fire command center

## Slide 28: Inspections and testing
…Detection and control verification
Primarily involves the fire alarm, mechanical, electrical, and controls subcontractors
Special Inspector tasks:
  Verifies the automatic sequence of operations
  Verifies manual sequence of operations through the firefighter’s smoke control panel
  Confirms supervision of power downstream of disconnects
  After completing all tests, issues a testing report to the engineer of record.
  Schedules final acceptance testing with the AHJ

## Slide 29: Smoke control system design and testing 101
Best Practices
Installation
And
Testing

## Slide 30: Best practices installation and testing
Step 1: Review the Rational Analysis (Smoke Control Report)
  Identify the different smoke control zones
  Confirm the type of smoke control in each zone (passive or mechanical)
  Determine equipment status verification requirements
  Study the sequence of operations
  Examine the smoke control panel layout
    If it is not in the report, check the mechanical plans.

## Slide 31: Best practices installation and testing
Step 2: Find out who is providing verification (positive status) devices and the type:
  Generally, fire alarm systems connect to verification devices provided by others. Includes:
    Fans (differential pressure switches, VFD contacts, or current relays)
    Dampers (limit switches, actuator contacts, other)
    Power downstream of disconnects (contact in the switch or by other means)
  Check the plans and specifications for requirements. If omitted, submit a request for information.

## Slide 32: Best practices installation and testing
Step 3: Where is conduit required?
  CBC Section 907.6.1.1 requires the fire alarm network in high-rise buildings to be, “Installed in enclosed continuous metallic raceways…” or in concrete.
  Section 909.12.2 states, “…all wiring, regardless of voltage, shall be enclosed within continuous raceway.”
  Confirm requirements with the Authority Having Jurisdiction

## Slide 33: Best practices installation and testing
Step 4: Prepare fire alarm shop drawings
  Determine quantities and locations of the following and show them on the shop drawings:
    Initiating devices activating the smoke control sequence of operations
    Control relays for fans, dampers, and other smoke control related equipment
    Positive status devices required by CBC Section 909.12.1
  Include:
    Fire fighters smoke control panel layout.
    Smoke control sequence of operations
    Connection details
    Conduit locations

## Slide 34: Best practices installation and testing
Step 5: Obtain separate approval of the smoke control panel layout. Typical approvals are required by:
Author of the rational analysis
Smoke control special inspector
Fire department inspector assigned to the project

## Slide 35: Firefighter’s smoke control panel

## Slide 36: Firefighter’s smoke control panel

## Slide 37: Firefighter’s smoke control panel

## Slide 38: Mechanical test panel (los angeles fire department)

## Slide 39: Mechanical test panel (los angeles fire department)

## Slide 40: Best practices installation and testing
Step 6: Clarify details related to the weekly self test required by CBC Section 909.12.1.
If disruptive to building operations, the weekly self test can be bypassed
Requires approval from the Authority Having Jurisdiction
If approved, dedicated smoke control fans and dampers must be tested bi-annually along with power supervision of bypassed components

## Slide 41: Best practices installation and testing
Step 7: Monitor progress in the field
Make regular site visits
Verify the installation of back boxes and enclosures needed for smoke control system interface
Coordinate with the general contractor in the fire command center, especially
  Fire rated back boards for mounting equipment
  Air conditioning
  Power
  Lighting

## Slide 42: Best practices installation and testing
Step 8: Inspect the physical connections of fire alarm control and status modules to their respective fans and dampers. Be sure to coordinate with:
  General contractor MEP Cordinator (if they have one)
  Mechanical subcontractor
  Electrical subcontractor
  Controls subcontractor

## Slide 43: Best practices installation and testing
Step 9: Pretest the system
Starts after permanent power is provided
Coordinate with the special inspector, general contractor and other trades
Use the smoke control panel to aid in pretesting
Test fans for on/off status and control
Test smoke control dampers for open/closed status and control
Test for supervision of power downstream of the disconnects.

## Slide 44: Best practices installation and testing
Step 10: Test the System
Automatic sequence of operations
Manual override from the smoke control panel
Test fault conditions
Check operation of white status indicators
Weekly self test (as required)
Coordinate with the special inspector, general contractor and other trades
Make room for the air balance subcontractor. They will need access to the system for measuring pressure differentials, exhaust and airflow rates

## Slide 45: Best practices installation and testing
Step 11: Final Acceptance
After the special inspector has accepted the system, be available to test the system again with the authority having jurisdiction. Additional changes may be required, depending on what they find.
Provide all required documentation, including test results, operating instructions, and as-built drawings. The special inspector will need those documents for their report to the Engineer of Record.

## Slide 46: smoke control design and testing 101
Thank You